## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-12-25
System Name: | COOS COUNTY PARKS LAVERNE |  |  | ID#: 41 | 94557 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 40 | 40 | 0 | 30 | 0.021
2 | 40 | 40 | 0 | 30 | 0.018
3 | 40 | 40 | 0 | 30 | 0.02
4 | 40 | 40 | 0 | 30 | 0.02
5 | 40 | 40 | 0 | 30 | 0.01
6 | 40 | 40 | 0 | 30 | 0.02
7 | 40 | 40 | 0 | 30 | 0.01
8 | 40 | 40 | 0 | 30 | 0.02
9 | 40 | 40 | 0 | 30 | 0.02
10 | 40 | 40 | 0 | 30 | 0.02
11 | 40 | 40 | 0 | 30 | 0.02
12 | 40 | 40 | 0 | 30 | 0.02
13 | 40 | 40 | 0 | 30 | 0.01
14 | 40 | 40 | 0 | 30 | 0.01
15 | 40 | 40 | 0 | 30 | 0.01
16 | 40 | 40 | 0 | 30 | 0.01
17 | 40 | 40 | 0 | 30 | 0.01
18 | 40 | 40 | 0 | 30 | 0.01
19 | 40 | 40 | 0 | 30 | 0.01
20 | 40 | 40 | 0 | 30 | 0.01
21 | 40 | 40 | 0 | 30 | 0.01
22 | 40 | 40 | 0 | 30 | 0.02
23 | 40 | 40 | 0 | 30 | 0.02
24 | 40 | 40 | 0 | 30 | 0.02
25 | 40 | 40 | 0 | 30 | 0.035
26 | 40 | 40 | 0 | 30 | 0.035
27 | 40 | 40 | 0 | 30 | 0.02
28 | 40 | 40 | 0 | 30 | 0.02
29 | 40 | 40 | 0 | 30 | 0.02
30 | 40 | 40 | 0 | 30 | 0.01
31 | 40 | 40 | 0 | 30 | 0.02
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | Caden Thurman
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | 12/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 5413962344
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Coos Co PKS LaVerne |  | ID#: 41 | 94557 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.8 | 104 | 83.2 | 8.1 | 7.41 | 24.6921 | YES
2 | 0.8 | 104 | 83.2 | 8.3 | 7 | 21.0854 | YES
3 | 0.8 | 104 | 83.2 | 8 | 7 | 21.5053 | YES
4 | 0.8 | 104 | 83.2 | 7.8 | 7.11 | 22.6505 | YES
5 | 0.8 | 104 | 83.2 | 7.5 | 7.4 | 25.6112 | YES
6 | 0.8 | 104 | 83.2 | 7.8 | 6.8 | 20.318 | YES
7 | 0.8 | 104 | 83.2 | 11 | 7 | 17.6925 | YES
8 | 1 | 104 | 104 | 12.4 | 7 | 16.5354 | YES
9 | 0.8 | 104 | 83.2 | 12 | 6.9 | 16.0438 | YES
10 | 0.8 | 104 | 83.2 | 12.7 | 6.9 | 14.9582 | YES
11 | 0.8 | 104 | 83.2 | 12.3 | 6.7 | 14.7224 | YES
12 | 0.8 | 104 | 83.2 | 10.8 | 6.7 | 16.1809 | YES
13 | 0.8 | 104 | 83.2 | 10.2 | 6.9 | 17.9991 | YES
14 | 0.8 | 104 | 83.2 | 10.7 | 6.8 | 16.8458 | YES
15 | 0.8 | 104 | 83.2 | 11.2 | 6.7 | 15.7762 | YES
16 | 0.8 | 104 | 83.2 | 10.8 | 6.7 | 16.1809 | YES
17 | 0.8 | 104 | 83.2 | 11.1 | 6.9 | 16.9894 | YES
18 | 0.8 | 104 | 83.2 | 10.7 | 7 | 18.0373 | YES
19 | 0.8 | 104 | 83.2 | 9.6 | 6.9 | 18.7101 | YES
20 | 0.8 | 104 | 83.2 | 9.4 | 7 | 19.6219 | YES
21 | 0.8 | 104 | 83.2 | 9.6 | 6.8 | 18.0771 | YES
22 | 0.5 | 104 | 52 | 9.2 | 7.2 | 20.6097 | YES
23 | 0.5 | 104 | 52 | 9.5 | 7.3 | 20.9267 | YES
24 | 0.7 | 104 | 72.8 | 9.7 | 7.4 | 21.8772 | YES
25 | 0.7 | 104 | 72.8 | 8.4 | 7.1 | 21.4511 | YES
26 | 0.8 | 104 | 83.2 | 8.2 | 6.6 | 18.4713 | YES
27 | 0.8 | 104 | 83.2 | 7.7 | 6.8 | 20.4514 | YES
28 | 0.8 | 104 | 83.2 | 7.4 | 7 | 22.3733 | YES
29 | 0.8 | 104 | 83.2 | 7.8 | 6.9 | 21.0399 | YES
30 | 0.8 | 104 | 83.2 | 8.1 | 6.8 | 19.9238 | YES
31 | 0.8 | 104 | 83.2 | 8.5 | 6.7 | 18.7517 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2