## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2026-01-02
System Name: | COOS COUNTY PARKS LAVERNE |  |  | ID#: 41 | 94557 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 40 | 40 | 0 | 30 | 0.012
2 | 40 | 40 | 0 | 30 | 0.012
3 | 40 | 40 | 0 | 30 | 0.013
4 | 40 | 40 | 0 | 30 | 0.013
5 | 40 | 40 | 0 | 30 | 0.012
6 | 40 | 40 | 0 | 30 | 0.013
7 | 40 | 40 | 0 | 30 | 0.016
8 | 40 | 40 | 0 | 30 | 0.013
9 | 40 | 40 | 0 | 30 | 0.013
10 | 40 | 40 | 0 | 30 | 0.013
11 | 40 | 40 | 0 | 30 | 0.012
12 | 40 | 40 | 0 | 30 | 0.013
13 | 40 | 40 | 0 | 30 | 0.013
14 | 40 | 40 | 0 | 30 | 0.013
15 | 40 | 40 | 0 | 30 | 0.013
16 | 40 | 40 | 0 | 30 | 0.013
17 | 42 | 42 | 0 | 30 | 0.019
18 | 44 | 44 | 0 | 30 | 0.015
19 | 42 | 42 | 0 | 30 | 0.013
20 | 40 | 40 | 0 | 30 | 0.013
21 | 40 | 40 | 0 | 30 | 0.013
22 | 40 | 40 | 0 | 30 | 0.012
23 | 40 | 40 | 0 | 30 | 0.013
24 | 40 | 40 | 0 | 30 | 0.014
25 | 40 | 40 | 0 | 30 | 0.015
26 | 40 | 40 | 0 | 30 | 0.013
27 | 40 | 40 | 0 | 30 | 0.013
28 | 40 | 40 | 0 | 30 | 0.014
29 | 40 | 40 | 0 | 30 | 0.02
30 | 40 | 40 | 0 | 30 | 0.012
31 | 40 | 40 | 0 | 30 | 0.012
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | Caden Thurman
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | 1/2026
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 5413962344
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Coos Co PKS LaVerne |  | ID#: 41 | 94557 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.8 | 104 | 83.2 | 8 | 6.92 | 20.9113 | YES
2 | 0.8 | 104 | 83.2 | 8.3 | 7.23 | 22.8605 | YES
3 | 0.8 | 104 | 83.2 | 9.2 | 6.72 | 18.0465 | YES
4 | 0.8 | 104 | 83.2 | 9.5 | 6.74 | 17.8232 | YES
5 | 0.8 | 104 | 83.2 | 9.1 | 7.2 | 21.4569 | YES
6 | 0.8 | 104 | 83.2 | 8.7 | 6.92 | 19.9752 | YES
7 | 0.8 | 104 | 83.2 | 8.9 | 7.25 | 22.1267 | YES
8 | 1 | 104 | 104 | 8.7 | 7.14 | 22.063 | YES
9 | 0.8 | 104 | 83.2 | 7 | 6.98 | 22.8119 | YES
10 | 0.8 | 104 | 83.2 | 7.1 | 6.77 | 21.05 | YES
11 | 0.8 | 104 | 83.2 | 6.9 | 6.85 | 21.9356 | YES
12 | 0.8 | 104 | 83.2 | 7 | 7 | 22.9735 | YES
13 | 0.8 | 104 | 83.2 | 6.8 | 7.16 | 24.6391 | YES
14 | 0.8 | 104 | 83.2 | 6.7 | 6.94 | 22.9435 | YES
15 | 0.8 | 104 | 83.2 | 6.8 | 6.98 | 23.1162 | YES
16 | 0.8 | 104 | 83.2 | 6.7 | 5.98 | 16.4538 | YES
17 | 1.4 | 104 | 145.6 | 6.6 | 6.42 | 20.589 | YES
18 | 0.9 | 104 | 93.6 | 6.2 | 6.48 | 20.406 | YES
19 | 0.8 | 104 | 83.2 | 6.7 | 6.96 | 23.1061 | YES
20 | 0.8 | 104 | 83.2 | 6.6 | 7 | 23.5914 | YES
21 | 0.8 | 104 | 83.2 | 6.8 | 7.13 | 24.3778 | YES
22 | 0.5 | 104 | 52 | 6.9 | 7 | 22.3531 | YES
23 | 0.5 | 104 | 52 | 6.7 | 6.34 | 18.0017 | YES
24 | 0.7 | 104 | 72.8 | 6.8 | 6.94 | 22.5352 | YES
25 | 0.7 | 104 | 72.8 | 6.4 | 6.86 | 22.496 | YES
26 | 0.8 | 104 | 83.2 | 6.6 | 6.84 | 22.2957 | YES
27 | 0.8 | 104 | 83.2 | 6.8 | 7.23 | 25.2607 | YES
28 | 0.8 | 104 | 83.2 | 6.9 | 7.28 | 25.5436 | YES
29 | 0.8 | 104 | 83.2 | 6.8 | 7.13 | 24.3778 | YES
30 | 1 | 104 | 104 | 6.8 | 7.34 | 26.8839 | YES
31 | 0.8 | 104 | 83.2 | 6.3 | 7.38 | 27.5632 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2