## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2026-02-02
System Name: | COOS COUNTY PARKS LAVERNE |  |  | ID#: 41 | 94557 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 40 | 40 | 0 | 30 | 0.02
2 | 40 | 40 | 0 | 30 | 0.01
3 | 40 | 40 | 0 | 30 | 0.01
4 | 40 | 40 | 0 | 30 | 0.01
5 | 40 | 40 | 0 | 30 | 0.02
6 | 40 | 40 | 0 | 30 | 0.013
7 | 40 | 40 | 0 | 30 | 0.01
8 | 40 | 40 | 0 | 30 | 0.013
9 | 40 | 40 | 0 | 30 | 0.013
10 | 40 | 40 | 0 | 30 | 0.013
11 | 40 | 40 | 0 | 30 | 0.012
12 | 40 | 40 | 0 | 30 | 0.013
13 | 40 | 40 | 0 | 30 | 0.03
14 | 40 | 40 | 0 | 30 | 0.02
15 | 40 | 40 | 0 | 30 | 0.02
16 | 40 | 40 | 0 | 30 | 0.02
17 | 42 | 42 | 0 | 30 | 0.01
18 | 44 | 44 | 0 | 30 | 0.01
19 | 42 | 42 | 0 | 30 | 0.013
20 | 35 | 35 | 0 | 30 | 0.02
21 | 41 | 41 | 0 | 30 | 0.02
22 | 40 | 40 | 0 | 30 | 0.01
23 | 40 | 40 | 0 | 30 | 0.02
24 | 40 | 40 | 0 | 30 | 0.02
25 | 40 | 40 | 0 | 30 | 0.02
26 | 40 | 40 | 0 | 30 | 0.02
27 | 40 | 40 | 0 | 30 | 0.013
28 | 40 | 40 | 0 | 30 | 0.014
29 |  |  |  | 30
30 |  |  |  | 30
31 |  |  |  | 30
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | Caden Thurman
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | 2/2026
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 5413962344
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Coos Co PKS LaVerne |  | ID#: 41 | 94557 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.8 | 104 | 83.2 | 7.9 | 6.6 | 18.8334 | YES
2 | 0.8 | 104 | 83.2 | 7.7 | 6.7 | 19.7519 | YES
3 | 0.8 | 104 | 83.2 | 7.5 | 6.6 | 19.3286 | YES
4 | 0.8 | 104 | 83.2 | 7.3 | 6.8 | 20.9946 | YES
5 | 0.8 | 104 | 83.2 | 7.3 | 6.6 | 19.5817 | YES
6 | 0.8 | 104 | 83.2 | 8.5 | 6.4 | 16.9196 | YES
7 | 0.8 | 104 | 83.2 | 9.7 | 6.5 | 16.2161 | YES
8 | 0.8 | 104 | 83.2 | 9.3 | 6.6 | 17.2096 | YES
9 | 0.8 | 104 | 83.2 | 9.1 | 6.7 | 18.0389 | YES
10 | 0.8 | 104 | 83.2 | 8.9 | 6.6 | 17.6567 | YES
11 | 0.8 | 104 | 83.2 | 9.1 | 6.5 | 16.8473 | YES
12 | 0.8 | 104 | 83.2 | 9.8 | 6.5 | 16.1136 | YES
13 | 1.2 | 104 | 124.8 | 9.4 | 6.4 | 16.6891 | YES
14 | 0.8 | 104 | 83.2 | 8.8 | 6.3 | 16.0466 | YES
15 | 1.2 | 104 | 124.8 | 8.5 | 6.5 | 18.2957 | YES
16 | 0.8 | 104 | 83.2 | 8.7 | 6.7 | 18.5106 | YES
17 | 1.2 | 104 | 124.8 | 8.3 | 6.6 | 19.1847 | YES
18 | 0.8 | 104 | 83.2 | 9.6 | 5.7 | 12.5218 | YES
19 | 0.8 | 104 | 83.2 | 9.2 | 6.7 | 17.9231 | YES
20 | 1.2 | 104 | 124.8 | 9.4 | 6.8 | 19.1421 | YES
21 | 1.2 | 104 | 124.8 | 9.5 | 6.7 | 18.3735 | YES
22 | 1 | 104 | 104 | 9.3 | 6.6 | 17.5916 | YES
23 | 1.4 | 104 | 145.6 | 9.1 | 6.8 | 19.9595 | YES
24 | 1.4 | 104 | 145.6 | 9.3 | 6.9 | 20.3983 | YES
25 | 1.4 | 104 | 145.6 | 9.1 | 7.2 | 22.963 | YES
26 | 1.2 | 104 | 124.8 | 9.3 | 6.5 | 17.378 | YES
27 | 1.2 | 104 | 124.8 | 9.8 | 6.4 | 16.2698 | YES
28 | 1.2 | 104 | 124.8 | 10.6 | 6.9 | 18.3329 | YES
29 |  | 104
30 |  | 104
31 |  | 104
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2