## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2026-03-02
System Name: | COOS COUNTY PARKS LAVERNE |  |  | ID#: 41 | 94557 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 40 | 40 | 0 | 30 | 0.013
2 | 40 | 40 | 0 | 30 | 0.015
3 | 40 | 40 | 0 | 30 | 0.018
4 | 40 | 40 | 0 | 30 | 0.017
5 | 40 | 40 | 0 | 30 | 0.014
6 | 40 | 40 | 0 | 30 | 0.013
7 | 40 | 40 | 0 | 30 | 0.016
8 | 40 | 40 | 0 | 30 | 0.014
9 | 40 | 40 | 0 | 30 | 0.021
10 | 41 | 41 | 0 | 30 | 0.018
11 | 40 | 40 | 0 | 30 | 0.016
12 | 40 | 40 | 0 | 30 | 0.017
13 | 40 | 40 | 0 | 30 | 0.015
14 | 40 | 40 | 0 | 30 | 0.016
15 | 40 | 40 | 0 | 30 | 0.013
16 | 40 | 40 | 0 | 30 | 0.016
17 | 40 | 40 | 0 | 30 | 0.017
18 | 40 | 40 | 0 | 30 | 0.021
19 | 40 | 40 | 0 | 30 | 0.018
20 | 40 | 40 | 0 | 30 | 0.019
21 | 40 | 40 | 0 | 30 | 0.01
22 | 40 | 40 | 0 | 30 | 0.021
23 | 40 | 40 | 0 | 30 | 0.017
24 | 40 | 40 | 0 | 30 | 0.016
25 | 40 | 40 | 0 | 30 | 0.015
26 | 40 | 40 | 0 | 30 | 0.012
27 | 40 | 40 | 0 | 30 | 0.014
28 | 40 | 40 | 0 | 30 | 0.019
29 | 40 | 40 | 0 | 30 | 0.021
30 | 40 | 40 | 0 | 30 | 0.016
31 | 40 | 40 | 0 | 30 | 0.018
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | Caden Thurman
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | 3/2026
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 5413962344
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Coos Co PKS LaVerne |  | ID#: 41 | 94557 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.2 | 104 | 124.8 | 10.6 | 6.4 | 15.467 | YES
2 | 1.2 | 104 | 124.8 | 11.2 | 6.7 | 16.4765 | YES
3 | 1.2 | 104 | 124.8 | 10.8 | 6.8 | 17.4883 | YES
4 | 1.2 | 104 | 124.8 | 10.5 | 6.6 | 16.6527 | YES
5 | 1.2 | 104 | 124.8 | 9.8 | 6.8 | 18.6522 | YES
6 | 1 | 104 | 104 | 9.4 | 6.8 | 18.7218 | YES
7 | 1 | 104 | 104 | 10.3 | 6.5 | 15.9536 | YES
8 | 1.2 | 104 | 124.8 | 11.4 | 6.2 | 13.7674 | YES
9 | 1.1 | 104 | 114.4 | 11 | 6.8 | 17.0773 | YES
10 | 1.2 | 104 | 124.8 | 8.8 | 6.9 | 20.6097 | YES
11 | 1 | 104 | 104 | 8.6 | 6.5 | 17.7815 | YES
12 | 1 | 104 | 104 | 8.9 | 6.6 | 18.05 | YES
13 | 1 | 104 | 104 | 9.2 | 6.4 | 16.5383 | YES
14 | 1 | 104 | 104 | 12.7 | 6.8 | 14.7461 | YES
15 | 1.2 | 104 | 124.8 | 10.3 | 6.9 | 18.6919 | YES
16 | 1 | 104 | 104 | 10 | 6.7 | 17.404 | YES
17 | 1 | 104 | 104 | 11.1 | 6.6 | 15.6864 | YES
18 | 1 | 104 | 104 | 10.4 | 6.6 | 16.3977 | YES
19 | 0.8 | 104 | 83.2 | 10.9 | 6.7 | 16.0786 | YES
20 | 1 | 104 | 104 | 13.5 | 6.8 | 13.9782 | YES
21 | 1 | 104 | 104 | 11.2 | 6.9 | 17.2549 | YES
22 | 1.2 | 104 | 124.8 | 13.3 | 6.7 | 13.9652 | YES
23 | 1.2 | 104 | 124.8 | 12.7 | 6.5 | 13.4959 | YES
24 | 1 | 104 | 104 | 11.3 | 6.8 | 16.5715 | YES
25 | 1 | 104 | 104 | 11.7 | 6.6 | 15.105 | YES
26 | 1 | 104 | 104 | 11.4 | 6.5 | 14.8861 | YES
27 | 1.2 | 104 | 124.8 | 12 | 6.7 | 15.662 | YES
28 | 1 | 104 | 104 | 11.7 | 6.7 | 15.6201 | YES
29 | 0.9 | 104 | 93.6 | 11.5 | 6.9 | 16.7431 | YES
30 | 0.8 | 104 | 83.2 | 11.9 | 6.8 | 15.6106 | YES
31 | 0.8 | 104 | 83.2 | 11.4 | 6.4 | 14.0958 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2