## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Coos
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | 0.8 | 2021-09-21
System Name: | Coos Co Parks-W.LaVerne |  |  | ID#: 41 | 94558 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.03
2 |  |  | 0.04
3 |  |  | 0.04
4 |  |  | 0.04
5 |  |  | 0.03
6 |  |  | 0.04
7 |  |  | 0.03
8 |  |  | 0.03
9 |  |  | 0.03
10 |  |  | 0.04
11 |  |  | 0.03
12 |  |  | 0.03
13 |  |  | 0.03
14 |  |  | 0.03
15 |  |  | 0.03
16 |  |  | 0.04
17 |  |  | 0.04
18 |  |  | 0.03
19 |  |  | 0.03
20 |  |  | 0.03
21 |  |  | 0.04
22 |  |  | n/a |  |  |  | Offline
23 |  |  | n/a
24 |  |  | n/a
25 |  |  | n/a
26 |  |  | n/a
27 |  |  | n/a
28 |  |  | n/a
29 |  |  | n/a
30 |  |  | n/a
31 |  |  | n/a
Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Calvin Napier
[5 empty] | SIGNATURE: |  |  | 2021-09-21
[5 empty] | SIGNATURE: |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : A
| Coos Co. Parks WLV. |  | ID#: 41 | 94558 | Month/Year: | 2021-09-21 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes /No | [GPM]
1 | 1 | 72 | 72 | 20.4 | 9 | 19.9194 | YES
2 | 1.2 | 72 | 86.4 | 20.6 | 9.1 | 20.8614 | YES
3 | 1 | 72 | 72 | 19.4 | 8.7 | 19.058 | YES
4 | 1 | 72 | 72 | 20 | 8.9 | 19.7151 | YES
5 | 1 | 72 | 72 | 19.7 | 8.8 | 19.3838 | YES
6 | 1 | 72 | 72 | 19.8 | 8.6 | 17.8859 | YES
7 | 1 | 72 | 72 | 19.8 | 8.5 | 17.2373 | YES
8 | 0.8 | 72 | 57.6 | 19.6 | 8.2 | 15.2811 | YES
9 | 0.8 | 72 | 57.6 | 18.8 | 8.6 | 18.6859 | YES
10 | 1 | 72 | 72 | 18.7 | 8.8 | 20.7131 | YES
11 | 1 | 72 | 72 | 20.5 | 8.8 | 18.381 | YES
12 | 1 | 72 | 72 | 20.2 | 8.7 | 18.0716 | YES
13 | 1 | 72 | 72 | 20.3 | 8.7 | 17.9519 | YES
14 | 1 | 72 | 72 | 19.6 | 8.9 | 20.2452 | YES
15 | 0.8 | 72 | 57.6 | 19.7 | 8.5 | 16.9624 | YES
16 | 0.8 | 72 | 57.6 | 19.6 | 9.8 | 27.5463 | YES
17 | 0.8 | 72 | 57.6 | 18.9 | 9 | 21.5092 | YES
18 | 0.8 | 72 | 57.6 | 18.2 | 8.6 | 19.4453 | YES
19 | 1 | 72 | 72 | 18.7 | 9.2 | 23.9941 | YES
20 | 1 | 72 | 72 | 19.6 | 9.2 | 22.6076 | YES
21 | 0.8 | 72 | 57.6 | 17.3 | 9.2 | 25.7321 | YES
22 | n/a | 72 | #VALUE! | n/a | n/a | #VALUE! | #VALUE! | Offline
23 | n/a | 72 | #VALUE! | n/a | n/a | #VALUE! | #VALUE! | Seasonal
24 | n/a | 72 | #VALUE! | n/a | n/a | #VALUE! | #VALUE! | Shutdown
25 | n/a | 72 | #VALUE! | n/a | n/a | #VALUE! | #VALUE!
26 | n/a | 72 | #VALUE! | n/a | n/a | #VALUE! | #VALUE!
27 | n/a | 72 | #VALUE! | n/a | n/a | #VALUE! | #VALUE!
28 | n/a | 72 | #VALUE! | n/a | n/a | #VALUE! | #VALUE!
29 | n/a | 72 | #VALUE! | n/a | n/a | #VALUE! | #VALUE!
30 | n/a | 72 | #VALUE! | n/a | n/a | #VALUE! | #VALUE!
31 | n/a | 72 | #VALUE! | n/a | n/a | #VALUE! | #VALUE!
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
yes
yes
yes
yes
Calvin Napier