## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Coos
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | 0.8 | 2023-06-22
System Name: | Coos Co Parks-W.LaVerne |  |  | ID#: 41 | 94558 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.03
2 |  |  | 0.03
3 |  |  | 0.03
4 |  |  | 0.02
5 |  |  | 0.02
6 |  |  | 0.02
7 |  |  | 0.02
8 |  |  | 0.02
9 |  |  | 0.03
10 |  |  | 0.03
11 |  |  | 0.02
12 |  |  | 0.03
13 |  |  | 0.03
14 |  |  | 0.03
15 |  |  | 0.03
16 |  |  | 0.03
17 |  |  | 0.03
18 |  |  | 0.03
19 |  |  | 0.03
20 |  |  | 0.03
21 |  |  | 0.03
22 |  |  | 0.03
23 |  |  | 0.03
24 |  |  | 0.03
25 |  |  | 0.03
26 |  |  | 0.03
27 |  |  | 0.03
28 |  |  | 0.03
29 |  |  | 0.03
30 |  |  | 0.03
31 | [6 empty] | Seasonal Shut down.
Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Calvin Napier
[5 empty] | SIGNATURE: |  |  | 2023-06-22
[5 empty] | SIGNATURE: |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : A
| Coos Co. Parks WLV. |  | ID#: 41 | 94558 | Month/Year: | 2023-06-22 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes /No | [GPM]
1 | 1.2 | 72 | 86.4 | 15.4 | 8 | 19.6408 | YES
2 | 1.2 | 72 | 86.4 | 15.2 | 8 | 19.9032 | YES
3 | 1 | 72 | 72 | 15.3 | 8 | 19.3285 | YES
4 | 1 | 72 | 72 | 15.2 | 7.9 | 18.7529 | YES
5 | 1 | 72 | 72 | 15.4 | 7.9 | 18.5054 | YES
6 | 1 | 72 | 72 | 15.4 | 7.9 | 18.5054 | YES
7 | 1 | 72 | 72 | 15.5 | 8 | 19.0736 | YES
8 | 1 | 72 | 72 | 15.6 | 8 | 18.9474 | YES
9 | 0.8 | 72 | 57.6 | 15.8 | 8.1 | 18.9648 | YES
10 | 0.8 | 72 | 57.6 | 15.8 | 8.1 | 18.9648 | YES
11 | 0.8 | 72 | 57.6 | 15.2 | 7.9 | 18.3322 | YES
12 | 0.8 | 72 | 57.6 | 15.4 | 7.7 | 16.8016 | YES
13 | 0.8 | 72 | 57.6 | 15.2 | 7.6 | 16.4086 | YES
14 | 0.8 | 72 | 57.6 | 15.7 | 7.6 | 15.8709 | YES
15 | 0.8 | 72 | 57.6 | 15.6 | 7.6 | 15.977 | YES
16 | 0.8 | 72 | 57.6 | 15.7 | 7.6 | 15.8709 | YES
17 | 1 | 72 | 72 | 15.6 | 7.8 | 17.5992 | YES
18 | 1 | 72 | 72 | 15.7 | 7.8 | 17.4825 | YES
19 | 1 | 72 | 72 | 15.7 | 7.9 | 18.1401 | YES
20 | 1 | 72 | 72 | 15.6 | 7.8 | 17.5992 | YES
21 | 1 | 72 | 72 | 15.6 | 7.6 | 16.3449 | YES
22 | 1 | 72 | 72 | 15.7 | 7.6 | 16.2363 | YES
23 | 1 | 72 | 72 | 15.6 | 7.8 | 17.5992 | YES
24 | 1 | 72 | 72 | 15.7 | 7.6 | 16.2363 | YES
25 | 1 | 72 | 72 | 15.6 | 7.7 | 16.9607 | YES
26 | 1 | 72 | 72 | 15.4 | 7.7 | 17.188 | YES
27 | 1 | 72 | 72 | 15.5 | 7.6 | 16.4541 | YES
28 | 1 | 72 | 72 | 15.6 | 7.7 | 16.9607 | YES
29 | 1 | 72 | 72 | 15.6 | 7.6 | 16.3449 | YES
30 | 1 | 72 | 72 | 15.7 | 7.6 | 16.2363 | YES
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
yes
yes
yes
yes
Calvin Napier