## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Coos
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | 0.8 | 2024-07-24
System Name: | Coos Co Parks-W. LaVerne |  |  | ID#: 41 | 94558 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.05
2 |  |  | 0.05
3 |  |  | 0.05
4 |  |  | 0.05
5 |  |  | 0.05
6 |  |  | 0.05
7 |  |  | 0.05
8 |  |  | 0.06
9 |  |  | 0.06
10 |  |  | 0.05
11 |  |  | 0.05
12 |  |  | 0.06
13 |  |  | 0.06
14 |  |  | 0.05
15 |  |  | 0.05
16 |  |  | 0.04
17 |  |  | 0.04
18 |  |  | 0.04
19 |  |  | 0.04
20 |  |  | 0.05
21 |  |  | 0.05
22 |  |  | 0.05
23 |  |  | 0.04
24 |  |  | 0.04
25 |  |  | 0.04
26 |  |  | 0.05
27 |  |  | 0.05
28 |  |  | 0.05
29 |  |  | 0.06
30 |  |  | 0.06
31 |  |  | 0.05
Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Calvin Napier
[5 empty] | SIGNATURE: |  |  | 2024-07-24
[5 empty] | SIGNATURE: |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : A
| Coos Co. Parks WLV. |  | ID#: 41 | 94558 | Month/Year: 9-23 | 2024-07-24 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes /No | [GPM]
1 | 1.8 | 72 | 129.6 | 17.5 | 7.3 | 14.1126 | YES
2 | 1.8 | 72 | 129.6 | 16.4 | 7.2 | 14.6358 | YES
3 | 1.6 | 72 | 115.2 | 16.2 | 7.1 | 13.9695 | YES
4 | 1.6 | 72 | 115.2 | 16.4 | 7.4 | 15.4072 | YES
5 | 1.6 | 72 | 115.2 | 16.8 | 7.5 | 15.5677 | YES
6 | 1.6 | 72 | 115.2 | 17.2 | 7.5 | 15.1577 | YES
7 | 1.4 | 72 | 100.8 | 17.6 | 7.2 | 12.9027 | YES
8 | 1.4 | 72 | 100.8 | 18.2 | 7.3 | 12.8641 | YES
9 | 1.4 | 72 | 100.8 | 18.9 | 7.5 | 13.2233 | YES
10 | 1.4 | 72 | 100.8 | 19.3 | 7.6 | 13.3617 | YES
11 | 1.4 | 72 | 100.8 | 19.7 | 7.4 | 12.0737 | YES
12 | 1.4 | 72 | 100.8 | 19.3 | 7.4 | 12.4025 | YES
13 | 1.2 | 72 | 86.4 | 18.8 | 7.1 | 11.2066 | YES
14 | 1.2 | 72 | 86.4 | 18.5 | 7.4 | 12.79 | YES
15 | 1.2 | 72 | 86.4 | 18.1 | 7.4 | 13.1377 | YES
16 | 1.2 | 72 | 86.4 | 17.5 | 7.2 | 12.6953 | YES
17 | 1.2 | 72 | 86.4 | 17.3 | 7.4 | 13.8607 | YES
18 | 1.2 | 72 | 86.4 | 17.7 | 7.3 | 13.0016 | YES
19 | 1 | 72 | 72 | 18.2 | 7.3 | 12.2877 | YES
20 | 1 | 72 | 72 | 18.7 | 7.4 | 12.3335 | YES
21 | 1 | 72 | 72 | 18.3 | 7.4 | 12.6692 | YES
22 | 1 | 72 | 72 | 18.5 | 7.6 | 13.4667 | YES
23 | 1 | 72 | 72 | 19.2 | 7.5 | 12.3795 | YES
24 | 1 | 72 | 72 | 19.1 | 7.4 | 12.0065 | YES
25 | 1 | 72 | 72 | 18.7 | 7.2 | 11.446 | YES
26 | 1 | 72 | 72 | 18.3 | 7.5 | 13.1499 | YES
27 | 0.8 | 72 | 57.6 | 18.5 | 7.4 | 12.2168 | YES
28 | 0.8 | 72 | 57.6 | 18.9 | 7.6 | 12.8138 | YES
29 | 0.8 | 72 | 57.6 | 18.4 | 7.2 | 11.414 | YES
30 | 0.8 | 72 | 57.6 | 18.1 | 7.4 | 12.5494 | YES
31 | 0.8 | 72 | 57.6 | 18.7 | 7.6 | 12.9868 | YES
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
yes
yes
yes
yes
Calvin Napier