## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Coos
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | 0.8 | 2024-08-24
System Name: | Coos Co Parks-W. LaVerne |  |  | ID#: 41 | 94558 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.04
2 |  |  | 0.05
3 |  |  | 0.05
4 |  |  | 0.06
5 |  |  | 0.04
6 |  |  | 0.05
7 |  |  | 0.05
8 |  |  | 0.05
9 |  |  | 0.05
10 |  |  | 0.05
11 |  |  | 0.05
12 |  |  | 0.04
13 |  |  | 0.05
14 |  |  | 0.05
15 |  |  | 0.05
16 |  |  | 0.04
17 |  |  | 0.04
18 |  |  | 0.05
19 |  |  | 0.05
20 |  |  | 0.05
21 |  |  | 0.05
22 |  |  | 0.05
23 |  |  | 0.05
24 |  |  | 0.06
25 |  |  | 0.04
26 |  |  | 0.05
27 |  |  | 0.04
28 |  |  | 0.04
29 |  |  | 0.04
30 |  |  | 0.04
31 |  |  | 0.04
Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Calvin Napier
[5 empty] | SIGNATURE: |  |  | 2024-08-24
[5 empty] | SIGNATURE: |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : A
| Coos Co. Parks WLV. |  | ID#: 41 | 94558 | Month/Year: 9-23 | 2024-08-24 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes /No | [GPM]
1 | 1 | 72 | 72 | 21.7 | 7.1 | 9 | YES
2 | 1 | 72 | 72 | 21.2 | 7.1 | 9.3108 | YES
3 | 1 | 72 | 72 | 21.6 | 7.1 | 9.0614 | YES
4 | 0.8 | 72 | 57.6 | 22.7 | 7.3 | 8.86 | YES
5 | 0.8 | 72 | 57.6 | 21.3 | 7.4 | 10.1161 | YES
6 | 0.8 | 72 | 57.6 | 19 | 7.5 | 12.2624 | YES
7 | 0.8 | 72 | 57.6 | 21.2 | 7.3 | 9.8091 | YES
8 | 0.8 | 72 | 57.6 | 22.1 | 7.2 | 8.8869 | YES
9 | 0.8 | 72 | 57.6 | 21.1 | 7.4 | 10.2538 | YES
10 | 0.8 | 72 | 57.6 | 21.8 | 7.5 | 10.154 | YES
11 | 0.8 | 72 | 57.6 | 19 | 7.5 | 12.2624 | YES
12 | 0.8 | 72 | 57.6 | 19.7 | 7.3 | 10.8555 | YES
13 | 0.8 | 72 | 57.6 | 20.5 | 7.2 | 9.9056 | YES
14 | 0.8 | 72 | 57.6 | 21.2 | 7.2 | 9.4469 | YES
15 | 0.8 | 72 | 57.6 | 22.1 | 7.1 | 8.5573 | YES
16 | 0.8 | 72 | 57.6 | 19.4 | 7.4 | 11.4995 | YES
17 | 0.8 | 72 | 57.6 | 19.1 | 7.5 | 12.1803 | YES
18 | 1.2 | 72 | 86.4 | 18.9 | 7.4 | 12.4513 | YES
19 | 1.4 | 72 | 100.8 | 19.7 | 7.6 | 13.0083 | YES
20 | 1.2 | 72 | 86.4 | 20.5 | 7.5 | 11.6071 | YES
21 | 1.2 | 72 | 86.4 | 19.1 | 7.6 | 13.2356 | YES
22 | 1 | 72 | 72 | 17.6 | 7.6 | 14.3026 | YES
23 | 1 | 72 | 72 | 17.3 | 7.4 | 13.5474 | YES
24 | 1 | 72 | 72 | 17.4 | 7.4 | 13.457 | YES
25 | 1 | 72 | 72 | 18.9 | 7.3 | 11.723 | YES
26 | 1 | 72 | 72 | 18.1 | 7.4 | 12.8403 | YES
27 | 1 | 72 | 72 | 18.6 | 7.4 | 12.4166 | YES
28 | 0.8 | 72 | 57.6 | 17.9 | 7.3 | 12.2535 | YES
29 | 0.8 | 72 | 57.6 | 18.2 | 7.4 | 12.4654 | YES
30 | 0.8 | 72 | 57.6 | 19.1 | 7.5 | 12.1803 | YES
31 | 0.8 | 72 | 57.6 | 17.8 | 7.6 | 13.7938 | YES
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
yes
yes
yes
yes
Calvin Napier