## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-06-01
System Name: | COOS COUNTY PARKS LAVERNE |  |  | ID#: 41 | 94558 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 43 | 43 | 0 | 30 | 0.019
2 | 42 | 42 | 0 | 30 | 0.018
3 | 40 | 40 | 0 | 30 | 0.019
4 | 42 | 42 | 0 | 30 | 0.018
5 | 40 | 40 | 0 | 30 | 0.018
6 | 40 | 40 | 0 | 30 | 0.017
7 | 43 | 43 | 0 | 30 | 0.017
8 | 43 | 43 | 0 | 30 | 0.018
9 | 42 | 42 | 0 | 30 | 0.017
10 | 43 | 43 | 0 | 30 | 0.019
11 | 43 | 43 | 0 | 30 | 0.017
12 | 45 | 45 | 0 | 30 | 0.017
13 | 42 | 42 | 0 | 30 | 0.02
14 | 43 | 43 | 0 | 30 | 0.02
15 | 41 | 41 | 0 | 30 | 0.02
16 | 43 | 43 | 0 | 30 | 0.02
17 | 41 | 41 | 0 | 30 | 0.02
18 | 42 | 42 | 0 | 30 | 0.02
19 | 41 | 41 | 0 | 30 | 0.02
20 | 42 | 42 | 0 | 30 | 0.02
21 | 41 | 41 | 0 | 30 | 0.02
22 | 41 | 41 | 0 | 30 | 0.02
23 | 42 | 42 | 0 | 30 | 0.02
24 | 41 | 41 | 0 | 30 | 0.02
25 | 41 | 41 | 0 | 30 | 0.02
26 | 42 | 42 | 0 | 30 | 0.02
27 | 42 | 42 | 0 | 30 | 0.02
28 | 41 | 41 | 0 | 30 | 0.02
29 | 41 | 41 | 0 | 30 | 0.02
30 | 41 | 41 | 0 | 30 | 0.02
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | Calvin Napier
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | 07/14/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 5413962344 |  | SWS317697
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | COOS COUNTY PARK LAVERN |  | ID#: 41 | 94557 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1 | 71 | 71 | 15 | 7.4 | 15.7978 | YES
2 | 1 | 71 | 71 | 16.3 | 7.2 | 13.4473 | YES
3 | 1 | 71 | 71 | 16.5 | 7.3 | 13.7711 | YES
4 | 1 | 71 | 71 | 16.9 | 7.4 | 13.915 | YES
5 | 1 | 71 | 71 | 16.9 | 7.2 | 12.9173 | YES
6 | 1 | 71 | 71 | 16.6 | 6.9 | 11.7851 | YES
7 | 1 | 71 | 71 | 16.7 | 6.9 | 11.7061 | YES
8 | 1 | 71 | 71 | 20.3 | 6.9 | 9.1786 | YES
9 | 1 | 71 | 71 | 21.4 | 7 | 8.8451 | YES
10 | 1 | 71 | 71 | 19.3 | 7.1 | 10.5884 | YES
11 | 1 | 71 | 71 | 17.9 | 7 | 11.209 | YES
12 | 0.9 | 71 | 63.9 | 15.3 | 7.3 | 14.7521 | YES
13 | 0.8 | 71 | 56.8 | 15.4 | 6.9 | 12.4848 | YES
14 | 0.8 | 71 | 56.8 | 16 | 6.8 | 11.552 | YES
15 | 0.8 | 71 | 56.8 | 19.4 | 7 | 9.8984 | YES
16 | 1 | 71 | 71 | 20.3 | 7.1 | 9.8963 | YES
17 | 1 | 71 | 71 | 16.9 | 6.8 | 11.1256 | YES
18 | 1 | 71 | 71 | 17.4 | 6.9 | 11.1672 | YES
19 | 0.8 | 71 | 56.8 | 16.4 | 6.9 | 11.6734 | YES
20 | 0.8 | 71 | 56.8 | 15.4 | 7.4 | 15.0352 | YES
21 | 0.8 | 71 | 56.8 | 16 | 7.4 | 14.4445 | YES
22 | 0.8 | 71 | 56.8 | 15 | 7.4 | 15.442 | YES
23 | 1 | 71 | 71 | 16.3 | 7.4 | 14.4847 | YES
24 | 1 | 71 | 71 | 16.4 | 7.5 | 14.9321 | YES
25 | 1 | 71 | 71 | 17.5 | 7.5 | 13.8735 | YES
26 | 1 | 71 | 71 | 18 | 7.4 | 12.9267 | YES
27 | 1 | 71 | 71 | 17.5 | 7.5 | 13.8735 | YES
28 | 1 | 71 | 71 | 19.1 | 7.4 | 12.0065 | YES
29 | 1 | 71 | 71 | 19 | 7.4 | 12.0875 | YES
30 | 1 | 71 | 71 | 19 | 6.7 | 9.2972 | YES
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2