## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-07-01
System Name: | COOS CO PKS WEST LAVERNE |  |  | ID#: 41 | 94558 | WTP ID: TP- | 4194558
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 30 | 30 | 0 | 30 | 0.02
2 | 30 | 30 | 0 | 30 | 0.019
3 | 30 | 30 | 0 | 30 | 0.02
4 | 30 | 30 | 0 | 30 | 0.021
5 | 30 | 30 | 0 | 30 | 0.02
6 | 30 | 30 | 0 | 30 | 0.02
7 | 30 | 30 | 0 | 30 | 0.02
8 | 30 | 30 | 0 | 30 | 0.02
9 | 35 | 35 | 0 | 30 | 0.02
10 | 40 | 40 | 0 | 30 | 0.02
11 | 40 | 40 | 0 | 30 | 0.02
12 | 40 | 40 | 0 | 30 | 0.03
13 | 40 | 40 | 0 | 30 | 0.03
14 | 40 | 40 | 0 | 30 | 0.021
15 | 40 | 40 | 0 | 30 | 0.02
16 | 30 | 30 | 0 | 30 | 0.02
17 | 36 | 36 | 0 | 30 | 0.02
18 | 33 | 33 | 0 | 30 | 0.02
19 | 40 | 40 | 0 | 30 | 0.02
20 | 33 | 33 | 0 | 30 | 0.02
21 | 33 | 33 | 0 | 30 | 0.02
22 | 33 | 33 | 0 | 30 | 0.03
23 | 38 | 38 | 0 | 30 | 0.02
24 | 38 | 38 | 0 | 30 | 0.02
25 | 33 | 33 | 0 | 30 | 0.02
26 | 34 | 34 | 0 | 30 | 0.02
27 | 40 | 40 | 0 | 30 | 0.02
28 | 34 | 34 | 0 | 30 | 0.02
29 | 40 | 34 | 6 | 30 | 0.02
30 | 38 | 38 | 0 | 30 | 0.02
31 | 40 | 40 | 0 | 30 | 0.02
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Calvin Napier
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | 07/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 396.2344 |  | CERT #:317697
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | COOS CO PKS- WEST LAVERN |  | ID#: 41 | 94557 | july/2025 |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.5 | 124 | 62 | 21.1 | 7.1 | 8.8461 | YES | 7
2 | 0.5 | 124 | 62 | 21.1 | 7 | 8.518 | YES | 7
3 | 0.5 | 124 | 62 | 19 | 7.2 | 10.5895 | YES | 7
4 | 0.5 | 124 | 62 | 15.9 | 7.4 | 14.0517 | YES | 7
5 | 0.5 | 124 | 62 | 16.8 | 7.1 | 11.8303 | YES | 7
6 | 1 | 124 | 124 | 17.8 | 7 | 11.2847 | YES | 7
7 | 1 | 124 | 124 | 18.2 | 6.9 | 10.5807 | YES | 7
8 | 1 | 124 | 124 | 17.4 | 6.9 | 11.1672 | YES | 7
9 | 1 | 124 | 124 | 21.7 | 7 | 8.6665 | YES | 7
10 | 1 | 124 | 124 | 19.7 | 6.8 | 9.2064 | YES | 7
11 | 1 | 124 | 124 | 19.2 | 6.8 | 9.524 | YES | 7
12 | 1 | 124 | 124 | 18.5 | 6.9 | 10.3685 | YES | 7
13 | 0.8 | 124 | 99.2 | 19.1 | 6.8 | 9.3693 | YES | 7
14 | 1 | 124 | 124 | 19.3 | 6.3 | 7.83 | YES | 7
15 | 1 | 124 | 124 | 19.5 | 7 | 10.0615 | YES | 7
16 | 1 | 124 | 124 | 20.1 | 7.2 | 10.4149 | YES | 7
17 | 0.8 | 124 | 99.2 | 18.3 | 7.1 | 11.0692 | YES | 7
18 | 0.8 | 124 | 99.2 | 19 | 7 | 10.1699 | YES | 7
19 | 0.8 | 124 | 99.2 | 17.8 | 6.8 | 10.2314 | YES | 7
20 | 0.8 | 124 | 99.2 | 17.1 | 7.1 | 12.0003 | YES | 7
21 | 0.8 | 124 | 99.2 | 18.2 | 7.1 | 11.1441 | YES | 7
22 | 0.8 | 124 | 99.2 | 18.9 | 6.9 | 9.8614 | YES | 7
23 | 0.8 | 124 | 99.2 | 19.5 | 6.9 | 9.4686 | YES | 7
24 | 0.8 | 124 | 99.2 | 19.3 | 7 | 9.9656 | YES | 7
25 | 0.9 | 124 | 111.6 | 19.4 | 7 | 10.0134 | YES | 7
26 | 1 | 124 | 124 | 18.3 | 6.9 | 10.5095 | YES | 7
27 | 1 | 124 | 124 | 18.7 | 6.6 | 9.1374 | YES | 7
28 | 1 | 124 | 124 | 18 | 6.5 | 9.2276 | YES | 7
29 | 1.2 | 124 | 148.8 | 18.9 | 6.8 | 9.947 | YES | 7
30 | 1 | 124 | 124 | 18.9 | 6.9 | 10.0919 | YES | 7
31 | 1 | 124 | 124 | 19.6 | 6.7 | 8.926 | YES | 7
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2