## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-08-25
System Name: | COOS CO PKS WEST LAVERNE |  |  | ID#: 41 | 94558 | WTP ID: TP- | 4194558
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 35 | 35 | 0 | 30 | 0.018
2 | 35 | 35 | 0 | 30 | 0.024
3 | 35 | 35 | 0 | 30 | 0.03
4 | 35 | 35 | 0 | 30 | 0.02
5 | 40 | 40 | 0 | 30 | 0.04
6 | 40 | 40 | 0 | 30 | 0.03
7 | 40 | 40 | 0 | 30 | 0.03
8 | 40 | 40 | 0 | 30 | 0.03
9 | 40 | 40 | 0 | 30 | 0.02
10 | 35 | 35 | 0 | 30 | 0.02
11 | 35 | 35 | 0 | 30 | 0.02
12 | 32 | 32 | 0 | 30 | 0.02
13 | 32 | 32 | 0 | 30 | 0.02
14 | 32 | 32 | 0 | 30 | 0.02
15 | 30 | 30 | 0 | 30 | 0.02
16 | 32 | 32 | 0 | 30 | 0.02
17 | 38 | 38 | 0 | 30 | 0.02
18 | 32 | 32 | 0 | 30 | 0.02
19 | 32 | 32 | 0 | 30 | 0.02
20 | 40 | 40 | 0 | 30 | 0.02
21 | 35 | 35 | 0 | 30 | 0.02
22 | 35 | 35 | 0 | 30 | 0.02
23 | 35 | 35 | 0 | 30 | 0.02
24 | 35 | 35 | 0 | 30 | 0.02
25 | 35 | 35 | 0 | 30 | 0.02
26 | 35 | 35 | 0 | 30 | 0.02
27 | 35 | 35 | 0 | 30 | 0.02
28 | 35 | 35 | 0 | 30 | 0.02
29 | 38 | 38 | 0 | 30 | 0.02
30 | 38 | 38 | 0 | 30 | 0.02
31 | 40 | 40 | 0 | 30 | 0.02
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Calvin Napier
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | 07/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 396.2344 |  | CERT #:317697
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | COOS CO PKS- WEST LAVERN |  | ID#: 41 | 94557 | july/2025 |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1 | 104 | 104 | 19.7 | 7.2 | 10.7 | YES | 7
2 | 0.8 | 104 | 83.2 | 19.6 | 7.3 | 10.9289 | YES | 7
3 | 1 | 104 | 104 | 19.3 | 6.8 | 9.4597 | YES | 7
4 | 1 | 104 | 104 | 19 | 7.1 | 10.8049 | YES | 7
5 | 1 | 104 | 104 | 17.8 | 7.1 | 11.7145 | YES | 7
6 | 0.8 | 104 | 83.2 | 20 | 7.1 | 9.8686 | YES | 7
7 | 1 | 104 | 104 | 20.9 | 7.2 | 9.8665 | YES | 7
8 | 1 | 104 | 104 | 18.9 | 7.1 | 10.878 | YES | 7
9 | 0.8 | 104 | 83.2 | 19.2 | 7.2 | 10.815 | YES | 7
10 | 1 | 104 | 104 | 21.3 | 7.2 | 9.6028 | YES | 7
11 | 1 | 104 | 104 | 21 | 7.1 | 9.438 | YES | 7
12 | 0.8 | 104 | 83.2 | 20.6 | 6.8 | 8.461 | YES | 7
13 | 0.8 | 104 | 83.2 | 20.7 | 6.8 | 8.4035 | YES | 7
14 | 0.5 | 104 | 52 | 20.6 | 7.1 | 9.1518 | YES | 7
15 | 0.5 | 104 | 52 | 22.6 | 6.8 | 7.1248 | YES | 7
16 | 0.6 | 104 | 62.4 | 21.3 | 6.8 | 7.8804 | YES | 7
17 | 0.6 | 104 | 62.4 | 21.6 | 6.9 | 8.0192 | YES | 7
18 | 0.6 | 104 | 62.4 | 19.2 | 7.1 | 10.1794 | YES | 7
19 | 0.6 | 104 | 62.4 | 18.9 | 6.7 | 8.9363 | YES | 7
20 | 0.5 | 104 | 52 | 19.5 | 7.2 | 10.2378 | YES | 7
21 | 0.5 | 104 | 52 | 19.6 | 6.8 | 8.7467 | YES | 7
22 | 0.5 | 104 | 52 | 21.5 | 7 | 8.2889 | YES | 7
23 | 0.5 | 104 | 52 | 20.3 | 7 | 8.9944 | YES | 7
24 | 0.6 | 104 | 62.4 | 19.3 | 7 | 9.7378 | YES | 7
25 | 0.6 | 104 | 62.4 | 21.4 | 7.2 | 9.106 | YES | 7
26 | 0.8 | 104 | 83.2 | 20.6 | 7.2 | 9.8388 | YES | 7
27 | 1 | 104 | 104 | 19.3 | 6.7 | 9.1098 | YES | 7
28 | 1 | 104 | 104 | 20.6 | 6.7 | 8.3386 | YES | 7
29 | 1 | 104 | 104 | 22.1 | 7 | 8.4336 | YES | 7
30 | 1 | 104 | 104 | 22.1 | 6.7 | 7.526 | YES | 7
31 | 0.9 | 104 | 93.6 | 22.3 | 7 | 8.223 | YES | 7
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2