## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-10-25
System Name: | COOS CO PKS WEST LAVERNE |  |  | ID#: 41 | 94558 | WTP ID: TP- | 4194558
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 40 | 40 | 0 | 30 | 0.023
2 | 40 | 40 | 0 | 30 | 0.02
3 | 40 | 40 | 0 | 30 | 0.02
4 | 40 | 40 | 0 | 30 | 0.02
5 | 40 | 40 | 0 | 30 | 0.02
6 | 40 | 40 | 0 | 30 | 0.02
7 | 40 | 40 | 0 | 30 | .02.
8 | 40 | 40 | 0 | 30 | 0.02
9 | 40 | 40 | 0 | 30 | 0.02
10 | 40 | 40 | 0 | 30 | 0.03
11 | 40 | 40 | 0 | 30 | 0.02
12 | 40 | 40 | 0 | 30 | 0.02
13 | 40 | 40 | 0 | 30 | 0.02
14 | 40 | 40 | 0 | 30 | 0.02
15 | 40 | 40 | 0 | 30 | 0.02
16 | 40 | 40 | 0 | 30 | 0.02
17 | OFFLINE | OFFLINE | #VALUE! | 30 | OFFLINE
18 | OFFLINE | OFFLINE | #VALUE! | 30 | OFFLINE
19 | OFFLINE | OFFLINE | #VALUE! | 30 | OFFLINE
20 | OFFLINE | OFFLINE | #VALUE! | 30 | OFFLINE
21 | OFFLINE | OFFLINE | #VALUE! | 30 | OFFLINE
22 | OFFLINE | OFFLINE | #VALUE! | 30 | OFFLINE
23 | OFFLINE | OFFLINE | #VALUE! | 30 | OFFLINE
24 | OFFLINE | OFFLINE | #VALUE! | 30 | OFFLINE
25 | OFFLINE | OFFLINE | #VALUE! | 30 | OFFLINE
26 | OFFLINE | OFFLINE | #VALUE! | 30 | OFFLINE
27 | OFFLINE | OFFLINE | 0 | 30 | OFFLINE
28 | OFFLINE | OFFLINE | #VALUE! | 30 | OFFLINE
29 | OFFLINE | OFFLINE | #VALUE! | 30 | OFFLINE
30 | OFFLINE | OFFLINE | #VALUE! | 30 | OFFLINE
31 | OFFLINE | OFFLINE | #VALUE! | 30 | OFFLINE
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Caden Thurman
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | 10/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 396.2344 |  | CERT #:317697
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | COOS CO PKS- WEST LAVERN |  | ID#: 41 | 94557 | july/2025 |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.8 | 104 | 83.2 | 17.9 | 6.8 | 10.1625 | YES | 7
2 | 0.8 | 104 | 83.2 | 17.8 | 6.9 | 10.6225 | YES | 7
3 | 0.8 | 104 | 83.2 | 17.1 | 6.8 | 10.7267 | YES | 7
4 | 0.8 | 104 | 83.2 | 17.9 | 6.9 | 10.551 | YES | 7
5 | 0.8 | 104 | 83.2 | 17.2 | 6.9 | 11.0612 | YES | 7
6 | 0.8 | 104 | 83.2 | 18.2 | 7.01 | 10.7748 | YES | 7
7 | 0.8 | 104 | 83.2 | 18.7 | 7.1 | 10.7747 | YES | 7
8 | 0.8 | 104 | 83.2 | 17.7 | 6.98 | 11.0198 | YES | 7
9 | 0.8 | 104 | 83.2 | 18.3 | 6.92 | 10.3472 | YES | 7
10 | 0.8 | 104 | 83.2 | 18.1 | 6.9 | 10.4095 | YES | 7
11 | 0.8 | 104 | 83.2 | 18 | 6.51 | 9.0501 | YES | 7
12 | 0.8 | 104 | 83.2 | 15.5 | 7.44 | 15.1583 | YES | 7
13 | 0.7 | 104 | 72.8 | 15.9 | 7.23 | 13.4963 | YES | 7
14 | 0.7 | 104 | 72.8 | 16.1 | 7.13 | 12.8301 | YES | 7
15 | 0.7 | 104 | 72.8 | 16.5 | 7.2 | 12.8204 | YES | 7
16 | 0.6 | 104 | 62.4 | 16.7 | 7 | 11.6059 | YES | 7
17 | OFFLINE | 104 | #VALUE! | OFFLINE | OFFLINE | #VALUE! | #VALUE! | 7
18 | OFFLINE | 104 | #VALUE! | OFFLINE | OFFLINE | #VALUE! | #VALUE! | 7
19 | OFFLINE | 104 | #VALUE! | OFFLINE | OFFLINE | #VALUE! | #VALUE! | 7
20 | OFFLINE | 104 | #VALUE! | OFFLINE | OFFLINE | #VALUE! | #VALUE! | 7
21 | OFFLINE | 104 | #VALUE! | OFFLINE | OFFLINE | #VALUE! | #VALUE! | 7
22 | OFFLINE | 104 | #VALUE! | OFFLINE | OFFLINE | #VALUE! | #VALUE! | 7
23 | OFFLINE | 104 | #VALUE! | OFFLINE | OFFLINE | #VALUE! | #VALUE! | 7
24 | OFFLINE | 104 | #VALUE! | OFFLINE | OFFLINE | #VALUE! | #VALUE! | 7
25 | OFFLINE | 104 | #VALUE! | OFFLINE | OFFLINE | #VALUE! | #VALUE! | 7
26 | OFFLINE | 104 | #VALUE! | OFFLINE | OFFLINE | #VALUE! | #VALUE! | 7
27 | OFFLINE | 104 | #VALUE! | OFFLINE | OFFLINE | #VALUE! | #VALUE! | 7
28 | OFFLINE | 104 | #VALUE! | OFFLINE | OFFLINE | #VALUE! | #VALUE! | 7
29 | OFFLINE | 104 | #VALUE! | OFFLINE | OFFLINE | #VALUE! | #VALUE! | 7
30 | OFFLINE | 104 | #VALUE! | OFFLINE | OFFLINE | #VALUE! | #VALUE! | 7
31 | OFFLINE | 104 | #VALUE! | OFFLINE | OFFLINE | #VALUE! | #VALUE! | 7
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2