## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Josephine
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-09-01
System Name: | Siskiyou Field Institute |  |  | ID#: 41 | 95360 |  | WTP : TP - | Takelma Creek
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0.038
2 |  |  |  | 0.04
3 |  |  |  | 0.04
4 |  |  |  | 0.04
5 |  |  |  | 0.038
6 |  |  |  | 0.04
7 |  |  |  | 0.04
8 |  |  |  | 0.04
9 |  |  |  | 0.04
10 |  |  |  | 0.04
11 |  |  |  | 0.04
12 |  |  |  | 0.04
13 |  |  |  | 0.04
14 |  |  |  | 0.04
15 |  |  |  | 0.039
16 |  |  |  | 0.04
17 |  |  |  | 0.04
18 |  |  |  | 0.04
19 |  |  |  | 0.04
20 |  |  |  | 0.04
21 |  |  |  | 0.04
22 |  |  |  | 0.04
23 |  |  |  | 0.038
24 |  |  |  | 0.04
25 |  |  |  | 0.04
26 |  |  |  | 0.04
27 |  |  |  | 0.04
28 |  |  |  | 0.04
29 |  |  |  | 0.04
30 |  |  |  | 0.04
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes |  | yes
Notes: |  |  |  |  | Lillie Hazelton
[5 empty] | LEH |  |  | 10.1.2023
[5 empty] | 5414159788 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Takelma Creek
System Name: | Siskiyou Field Institute |  | ID#: 41 | 95360 | Month/Year: | 2023-09-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.5 | 76.4 | 38.2 | 15 | 8.2 | 20.0561 | YES | 3.39
2 | 0.5 | 71.15 | 35.575 | 15 | 8.2 | 20.0561 | YES | 3.64
3 | 0.5 | 73.37 | 36.685 | 15 | 8.2 | 20.0561 | YES | 3.53
4 | 0.5 | 71.74 | 35.87 | 15 | 8.2 | 20.0561 | YES | 3.61
5 | 0.5 | 72.54 | 36.27 | 15 | 8.2 | 20.0561 | YES | 3.52
6 | 0.5 | 70.57 | 35.285 | 15 | 8.2 | 20.0561 | YES | 3.67
7 | 0.5 | 76.17 | 38.085 | 15 | 8.2 | 20.0561 | YES | 3.4
8 | 0.5 | 73.37 | 36.685 | 20 | 8.2 | 14.3778 | YES | 3.5
9 | 0.5 | 72.54 | 36.27 | 20 | 8.2 | 14.3778 | YES | 3.57
10 | 0.5 | 71.94 | 35.97 | 20 | 8.2 | 14.3778 | YES | 3.6
11 | 0.5 | 74.42 | 37.21 | 20 | 8.2 | 14.3778 | YES | 3.5
12 | 0.5 | 72.75 | 36.375 | 20 | 8.2 | 14.3778 | YES | 3.5
13 | 0.5 | 70.19 | 35.095 | 20 | 8.2 | 14.3778 | YES | 3.7
14 | 0.5 | 71.54 | 35.77 | 20 | 8.2 | 14.3778 | YES | 3.6
15 | 0.5 | 72.95 | 36.475 | 20 | 8.2 | 14.3778 | YES | 3.55
16 | 0.5 | 74.42 | 37.21 | 20 | 8.2 | 14.3778 | YES | 3.48
17 | 0.5 | 74 | 37 | 20 | 8.2 | 14.3778 | YES | 3.5
18 | 0.5 | 74.21 | 37.105 | 20 | 8.2 | 14.3778 | YES | 3.49
19 | 0.5 | 70.95 | 35.475 | 15 | 8.3 | 20.8083 | YES | 3.65
20 | 0.5 | 72.21 | 36.105 | 15 | 8.2 | 20.0561 | YES | 3.49
21 | 0.5 | 72.95 | 36.475 | 15 | 8.2 | 20.0561 | YES | 3.55
22 | 0.5 | 71.94 | 35.97 | 15 | 8.2 | 20.0561 | YES | 3.6
23 | 0.5 | 73.78 | 36.89 | 15 | 8.2 | 20.0561 | YES | 3.51
24 | 0.5 | 74.42 | 37.21 | 15 | 8.2 | 20.0561 | YES | 3.48
25 | 0.5 | 73.78 | 36.89 | 15 | 8.2 | 20.0561 | YES | 3.51
26 | 0.5 | 74.85 | 37.425 | 15 | 8.2 | 20.0561 | YES | 3.46
27 | 0.5 | 71.94 | 35.97 | 15 | 8.2 | 20.0561 | YES | 3.6
28 | 0.5 | 73.37 | 36.685 | 15 | 8.2 | 20.0561 | YES | 3.53
29 | 0.5 | 74.21 | 37.105 | 15 | 8.2 | 20.0561 | YES | 3.49
30 | 0.5 | 74 | 37 | 15 | 8.2 | 20.0561 | YES | 3.5
31 | 0.5 | 74.63 | 37.315 | 15 | 8.2 | 20.0561 | YES | 3.47
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2