## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Josephine
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-10-01
System Name: | Siskiyou Field Institute |  |  | ID#: 41 | 95360 |  | WTP : TP - | Takelma Creek
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0.04
2 |  |  |  | 0.04
3 |  |  |  | 0.04
4 |  |  |  | 0.037
5 |  |  |  | 0.04
6 |  |  |  | 0.04
7 |  |  |  | 0.04
8 |  |  |  | 0.04
9 |  |  |  | 0.04
10 |  |  |  | 0.04
11 |  |  |  | 0.04
12 |  |  |  | 0.04
13 |  |  |  | 0.04
14 |  |  |  | 0.04
15 |  |  |  | 0.04
16 |  |  |  | 0.04
17 |  |  |  | 0.04
18 |  |  |  | 0.04
19 |  |  |  | 0.04
20 |  |  |  | 0.04
21 |  |  |  | 0.04
22 |  |  |  | 0.04
23 |  |  |  | 0.04
24 |  |  |  | 0.04
25 |  |  |  | 0.04
26 |  |  |  | 0.04
27 |  |  |  | 0.04
28 |  |  |  | 0.04
29 |  |  |  | 0.04
30 |  |  |  | 0.04
31 |  |  |  | 0.04
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | YES |  | YES
Notes: |  |  |  |  | Lillie Hazelton
[5 empty] | LEH |  |  | 11.1.23
[5 empty] | 5414159788 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Takelma Creek
System Name: | Siskiyou Field Institute |  | ID#: 41 | 95360 | Month/Year: | 2023-10-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.5 | 76.4 | 38.2 | 15 | 8.2 | 20.0561 | YES | 3.39
2 | 0.5 | 75.73 | 37.865 | 15 | 8.2 | 20.0561 | YES | 3.42
3 | 0.5 | 72.34 | 36.17 | 15 | 8.2 | 20.0561 | YES | 3,58
4 | 0.5 | 72.54 | 36.27 | 15 | 8.2 | 20.0561 | YES | 3.57
5 | 0.5 | 73.72 | 36.86 | 15 | 8.2 | 20.0561 | YES | 3.51
6 | 0.5 | 75.95 | 37.975 | 15 | 8.2 | 20.0561 | YES | 3.41
7 | 0.5 | 71.94 | 35.97 | 15 | 8.2 | 20.0561 | YES | 3.6
8 | 0.5 | 73.57 | 36.785 | 15 | 8.2 | 20.0561 | YES | 3.52
9 | 0.5 | 76.62 | 38.31 | 15 | 8.2 | 20.0561 | YES | 3.38
10 | 0.5 | 76.17 | 38.085 | 15 | 8.2 | 20.0561 | YES | 3.4
11 | 0.5 | 77.31 | 38.655 | 15 | 8.2 | 20.0561 | YES | 3.35
12 | 0.5 | 78.96 | 39.48 | 15 | 8.2 | 20.0561 | YES | 3.28
13 | 0.5 | 80.68 | 40.34 | 10 | 8.2 | 27.8544 | YES | 3.21
14 | 0.5 | 76.85 | 38.425 | 10 | 8.2 | 27.8544 | YES | 3.37
15 | 0.5 | 76.17 | 38.085 | 10 | 8.2 | 27.8544 | YES | 3.4
16 | 0.5 | 75.29 | 37.645 | 10 | 8.2 | 27.8544 | YES | 3.44
17 | 0.5 | 74.63 | 37.315 | 10 | 8.2 | 27.8544 | YES | 3.47
18 | 0.5 | 74.21 | 37.105 | 15 | 8.2 | 20.0561 | YES | 3.49
19 | 0.5 | 74.72 | 37.36 | 15 | 8.2 | 20.0561 | YES | 3.49
20 | 0.5 | 73.16 | 36.58 | 15 | 8.2 | 20.0561 | YES | 3.54
21 | 0.5 | 74.85 | 37.425 | 10 | 8.2 | 27.8544 | YES | 3.46
22 | 0.5 | 79.44 | 39.72 | 10 | 8.2 | 27.8544 | YES | 3.26
23 | 0.5 | 76.17 | 38.085 | 10 | 8.2 | 27.8544 | YES | 3.4
24 | 0.5 | 76.62 | 38.31 | 10 | 8.2 | 27.8544 | YES | 3.38
25 | 0.5 | 79.2 | 39.6 | 10 | 8.2 | 27.8544 | YES | 3.27
26 | 0.5 | 79.2 | 39.6 | 10 | 8.2 | 27.8544 | YES | 3.27
27 | 0.5 | 74.85 | 37.425 | 10 | 8.2 | 27.8544 | YES | 3.46
28 | 0.5 | 78.48 | 39.24 | 10 | 8.2 | 27.8544 | YES | 3.3
29 | 0.5 | 79.69 | 39.845 | 10 | 8.2 | 27.8544 | YES | 3.25
30 | 0.5 | 78.48 | 39.24 | 10 | 8.2 | 27.8544 | YES | 3.3
31 | 0.5 | 76.17 | 38.085 | 10 | 8.2 | 27.8544 | YES | 3.4
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2