## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Josephine
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-02-01
System Name: | Siskiyou Field Institute |  |  | ID#: 41 | 95360 | WTP ID: TP- | Takelma Creek
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | NA |  | #VALUE! |  | NA | System Off for Takelma Diversion Work
2 | 30 |  | 30 | 15 | 0.03 | Mitt drained, back on, filling at noon
3 | 38 |  | 38 | 15 | 0.05 | heavy rain
4 | 38 |  | 38 | 15 | 0.076 | heavy rain
5 | 38 |  | 38 | 15 | ,131 | heavy rain
6 | 38 |  | 38 | 15 | 0.72 | heavy rain
7 | 30 |  | 30 | 15 | 0.17 | Takekma Creek Work
8 | 38 |  | 38 | 15 | 0.16 | Takekma Creek Work
9 | 38 |  | 38 | 15 | 0.142
10 | 38 |  | 38 | 15 | 0.172
11 | 38 |  | 38 | 15 | 0.132 | Mitt had water off til
12 | 38 |  | 38 | 15 | 0.14 | water back on 5pm
13 | 38 |  | 38 | 15 | 0.14 | heavy rain
14 | 38 |  | 38 | 15 | 0.21 | heavy rain
15 | 38 |  | 38 | 15 | 0.13 | heavy rain
16 | 38 |  | 38 | 15 | 0.13 | heavy rain
17 | 38 |  | 38 | 15 | 0.14 | heavy rain
18 | 38 |  | 38 | 15 | ,14 | heavy rain
19 | 38 |  | 38 | 15 | 0.056 | heavy rain
20 | NA |  | #VALUE! | NA | NA | water off for creek work
21 | NA |  | #VALUE! | NA | NA | water off for creek work
22 | 38 |  | 38 | 15 | 0.302 | water work water on
23 | 38 |  | 38 | 15 | 0.146 | sunny warm
24 | 38 |  | 38 | 15 | 0.15 | sunny warm
25 | 38 |  | 38 | 15 | 0.13 | sunny warm
26 | 38 |  | 38 | 15 | 0.124 | New PH&Temp tool
27 | 38 |  | 38 | 15 | 0.298 | cold and rainy
28 | 38 |  | 38 | 15 | 0.39 | snow
29 | 38 |  | 38 | 15 | 0.4 | snow
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | Lillie Hazelton
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | LEH |  | 2024-02-01
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 541 415-9788 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Takelma
System Name: | Siskiyou Field Institute |  | ID#: 41 | 95360 | Month/Year: | 2024-02-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | NA | NA | #VALUE! | 5 | 8.2 | #VALUE! | #VALUE! | NA
2 | 0.5 | 78.48 | 39.24 | 5 | 8.2 | 39.1912 | YES | 3.3
3 | 0.5 | 74 | 37 | 10 | 8.2 | 27.8544 | YES | 3.5
4 | 0.5 | 72.75 | 36.375 | 10 | 8.2 | 27.8544 | YES | 3.56
5 | 0.5 | 75.07 | 37.535 | 10 | 8.2 | 27.8544 | YES | 3.45
6 | 0.5 | 77.77 | 38.885 | 10 | 8.2 | 27.8544 | YES | 3.33
7 | 0.5 | 85.47 | 42.735 | 5 | 8.2 | 39.1912 | YES | 3.03
8 | 0.5 | 79.69 | 39.845 | 5 | 8.2 | 39.1912 | YES | 3.25
9 | 0.5 | 75.51 | 37.755 | 10 | 8.2 | 27.8544 | YES | 3.43
10 | 0.5 | 74.85 | 37.425 | 10 | 8.2 | 27.8544 | YES | 3.46
11 | 0.5 | 75.07 | 37.535 | 10 | 8.2 | 27.8544 | YES | 3.45
12 | 0.5 | 75.73 | 37.865 | 10 | 8.2 | 27.8544 | YES | 3.42
13 | 0.5 | 75.07 | 37.535 | 10 | 8.2 | 27.8544 | YES | 3.45
14 | 0.5 | 71.94 | 35.97 | 10 | 8.2 | 27.8544 | YES | 3.6
15 | 0.5 | 70 | 35 | 10 | 8.2 | 27.8544 | YES | 3.7
16 | 0.5 | 71.94 | 35.97 | 10 | 8.2 | 27.8544 | YES | 3.6
17 | 0.5 | 74 | 37 | 10 | 8.2 | 27.8544 | YES | 3.5
18 | 0.5 | 68.15 | 34.075 | 10 | 8.2 | 27.8544 | YES | 3.8
19 | 0.5 | 70.18 | 35.09 | 10 | 8.2 | 27.8544 | YES | 3.69
20 | 0.5 | NA | #VALUE! | NA | 8.2 | #VALUE! | #VALUE! | NA
21 | 0.5 | NA | #VALUE! | NA | 8.2 | #VALUE! | #VALUE! | NA
22 | 0.5 | 71.94 | 35.97 | 10 | 8.2 | 27.8544 | YES | 3.6
23 | 0.5 | 72.54 | 36.27 | 10 | 8.2 | 27.8544 | YES | 3.57
24 | 0.5 | 72.75 | 36.375 | 10 | 8.2 | 27.8544 | YES | 3.56
25 | 0.5 | 71.54 | 35.77 | 10 | 8.2 | 27.8544 | YES | 3.62
26 | 0.5 | 68.7 | 34.35 | 10 | 8 | 25.9281 | YES | 3.77
27 | 0.5 | 68.15 | 34.075 | 8.3 | 7.81 | 27.1536 | YES | 3.8
28 | 0.5 | 70 | 35 | 8 | 7.8 | 27.6085 | YES | 3.7
29 | 0.5 | 66.41 | 33.205 | 8 | 7.81 | 27.7079 | YES | 3.9
30
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
PAGE 2 of 2