## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Josephine
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-04-01
System Name: | Siskiyou Field Institute |  |  | 41-95360 |  | Takelma Creek | 0.5
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 38 |  | 38 | 15 | 0.554 | sunny
2 | 38 |  | 38 |  | 0.347 | sunny
3 | 38 |  | 38 |  | 0.39 | cloudy
4 | 38 |  | 38 |  | 0.114 | cloudy
5 | 38 |  | 38 |  | 0.506 | cloudy
6 | 38 |  | 38 |  | 0.736 | cloudy
7 | 38 |  | 38 |  | 0.32 | cloudy
8 | 38 |  | 38 |  | 0.77 | sunny
9 | 38 |  | 38 |  | 0.68 | cloudy
10 | 38 |  | 38 |  | 0.45 | sunny
11 | 38 |  | 38 |  | 0.098 | sunny
12 | 38 |  | 38 |  | 0.304 | partly cloudy
13 | 38 |  | 38 |  | 0.08 | cloudy, drizzle
14 | 38 |  | 38 |  | 0.186 | cloudy, drizzle
15 | 38 |  | 38 |  | 0.205 | cloudy
16 | 38 |  | 38 |  | 0.402 | partly cloudy
17 | 38 |  | 38 |  | 0.046 | sunny
18 | 38 |  | 38 |  | 0.089 | sunny
19 | 38 |  | 38 |  | 0.929 | sunny
20 | 38 |  | 38 |  | 0.048 | cloudy, breezy
21 | 38 |  | 38 |  | 0.038 | partly cloudy
22 | 38 |  | 38 |  | 0.044 | sunny
23 | 38 |  | 38 |  | 0.045 | sunny
24 | 38 |  | 38 |  | 0.043 | sunny
25 | 38 |  | 38 |  | 0.056 | cloudy
26 | 38 |  | 38 |  | 0.067 | cloudy
27 | 38 |  | 38 |  | 0.052 | cloudy
28 | 38 |  | 38 |  | 0.042 | mostly cloudy
29 | 38 |  | 38 |  | 0.067 | cloudy
30 | 38 |  | 38 |  | 0.038 | cloudy
31 | 38 |  | 38 |  | 0.038 | cloudy
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | Lillie Hazelton
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | LEH |  | 2024-04-01
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 541 415-9788 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | Takelma Creek
System Name: | Siskiyou Fiels Institute |  | ID#: 41 95360 |  | Month/Year: | 2024-04-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.5 | 69.62 | 34.81 | 13.5 | 8.38 | 23.6664 | YES | 3.72
2 | 0.5 | 68.7 | 34.35 | 16.1 | 8.5 | 20.8232 | YES | 3.77
3 | 0.5 | 68.52 | 34.3 | 14.1 | 8.76 | 26.15 | YES | 3.78
4 | 0.5 | 69.25 | 34.625 | 12.9 | 8.69 | 27.588 | YES | 3.74
5 | 0.55 | 70.02 | 38.511 | 13.6 | 8.68 | 26.3947 | YES | 3.69
6 | 0.54 | 70.57 | 38.1078 | 10.7 | 8.61 | 30.9444 | YES | 3.67
7 | 0.53 | 70.57 | 37.4021 | 10.2 | 8.72 | 33.2841 | YES | 3.67
8 | 0.54 | 70.96 | 38.3184 | 10.6 | 8.62 | 31.2688 | YES | 3.65
9 | 0.5 | 71.15 | 35.575 | 15.1 | 8.77 | 24.5686 | YES | 3.64
10 | 0.54 | 71.55 | 38.637 | 12.9 | 8.56 | 26.4234 | YES | 3.62
11 | 0.54 | 70.38 | 38.0052 | 14.63 | 8.61 | 24.0063 | YES | 3.68
12 | 0.54 | 70 | 37.8 | 14.3 | 8.67 | 25.0819 | YES | 3.7
13 | 0.52 | 70.96 | 36.8992 | 14.3 | 8.7 | 25.3023 | YES | 3.65
14 | 0.54 | 70.38 | 38.0052 | 13.5 | 8.66 | 26.3457 | YES | 3.68
15 | 0.53 | 70.96 | 37.6088 | 11.6 | 8.66 | 29.6072 | YES | 3.65
16 | 0.5 | 71.15 | 35.575 | 15.5 | 8.42 | 21.0391 | YES | 3.64
17 | 0.5 | 69.25 | 34.625 | 14.9 | 8.49 | 22.4628 | YES | 3.74
18 | 0.54 | 70.19 | 37.9026 | 12.4 | 8.66 | 28.0803 | YES | 3.69
19 | 0.54 | 69.81 | 37.6974 | 14.4 | 8.53 | 23.6686 | YES | 3.71
20 | 0.54 | 69.81 | 37.6974 | 14.4 | 8.58 | 24.1071 | YES | 3.71
21 | 0.54 | 70.19 | 37.9026 | 13.3 | 8.43 | 24.5362 | YES | 3.69
22 | 0.54 | 69.81 | 37.6974 | 14.4 | 8.31 | 21.8304 | YES | 3.71
23 | 0.5 | 69.62 | 34.81 | 15.9 | 8.44 | 20.6401 | YES | 3.72
24 | 0.5 | 70.19 | 35.095 | 15 | 8.45 | 21.9889 | YES | 3.69
25 | 0.54 | 70.19 | 37.9026 | 14 | 8.43 | 23.4267 | YES | 3.69
26 | 0.54 | 70.38 | 38.0052 | 13.6 | 8.52 | 24.8623 | YES | 3.68
27 | 0.54 | 70.96 | 38.3184 | 12.2 | 8.57 | 27.5558 | YES | 3.65
28 | 0.54 | 70.96 | 38.3184 | 12.2 | 8.37 | 25.6519 | YES | 3.65
29 | 0.54 | 70.96 | 38.3184 | 13.1 | 8.35 | 24.1432 | YES | 3.65
30 | 0.5 | 71.34 | 35.67 | 12.6 | 8.63 | 27.5276 | YES | 3.63
31 | 0.5 | 75.07 | 37.535 | 12 | 8 | 22.6938 | YES | 3.45
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2