## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County:
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-09-01
System Name: | Siskiyou Field Institute |  |  | ID#: 41 | 95360 | WTP ID: TP-A | Takelma Creek
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 38 |  | 38 | 15 | 0.05
2 | 38 |  | 38 |  | 0.05
3 | 38 |  | 38 |  | 0.04
4 | 38 |  | 38 |  | 0.04
5 | 38 |  | 38 |  | 0.05
6 | 38 |  | 38 |  | 0.05
7 | 38 |  | 38 |  | 0.05
8 | 38 |  | 38 |  | 0.04
9 | 38 |  | 38 |  | 0.04
10 | 38 |  | 38 |  | 0.05
11 | 38 |  | 38 |  | 0.05
12 | 38 |  | 38 |  | 0.04
13 | 38 |  | 38 |  | 0.04
14 | 38 |  | 38 |  | 0.05
15 | 38 |  | 38 |  | 0.05
16 | 38 |  | 38 |  | 0.05
17 | 38 |  | 38 |  | 0.04
18 | 38 |  | 38 |  | 0.03
19 | 38 |  | 38 |  | 0.04
20 | 38 |  | 38 |  | 0.04
21 | 38 |  | 38 |  | 0.03
22 | 38 |  | 38 |  | 0.04
23 | 38 |  | 38 |  | 0.04
24 | 38 |  | 38 |  | 0.03
25 | 38 |  | 38 |  | 0.04
26 | 38 |  | 38 |  | 0.03
27 | 38 |  | 38 |  | 0.04
28 | 38 |  | 38 |  | 0.04
29 | 38 |  | 38 |  | 0.04
30 | 38 |  | 38 |  | 0.04
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | No | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Lillie Hazelton
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | Rev Kent Downs 9/15/2024 |  | DATE: Sept 2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 415-9788 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Takelma
System Name: | Siskiyou Field Institute |  | ID#: 41 | 95360 | Month/Year: | 2024-09-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.5 | 60.5 | 30.25 | 24.3 | 10 | 21.0044 | YES | 3.98
2 | 0.5 | 65.23 | 32.615 | 23.3 | 10.5 | 26.9627 | YES | 3.97
3 | 0.5 | 63.25 | 31.625 | 23.9 | 11 | 31.123 | YES | 4.09
4 | 0.5 | 67.09 | 33.545 | 28.7 | 12 | 32.7065 | YES | 3.86
5 | 0.5 | 68.15 | 34.075 | 29 | 12 | 32.067 | YES | 3.8
6 | 0.5 | 70 | 35 | 27 | 11 | 25.3687 | YES | 3.7
7 | 0.5 | 68.15 | 34.075 | 27.5 | 11 | 24.5444 | YES | 3.8
8 | 0.5 | 67.8 | 33.9 | 24.3 | 11 | 30.3138 | YES | 3.82
9 | 0.5 | 68.15 | 34.075 | 24 | 11 | 30.9187 | YES | 3.8
10 | 0.5 | 69.15 | 34.575 | 23 | 10.7 | 29.5912 | YES | 3.75
11 | 0.5 | 68.1 | 34.05 | 22.6 | 11 | 33.9032 | YES | 3.8
12 | 0.5 | 69.81 | 34.905 | 20 | 11 | 40.2206 | NO | 3.71
13 | 0.5 | 68.51 | 34.255 | 19.1 | 10 | 29.6152 | YES | 3.78
14 | 0.5 | 70 | 35 | 18 | 10 | 31.8405 | YES | 3.7
15 | 0.5 | 74 | 37 | 17.4 | 10 | 33.1231 | YES | 3.5
16 | 0.5 | 72.14 | 36.07 | 17 | 10 | 34.0063 | YES | 3.59
17 | 0.5 | 70.18 | 35.09 | 18.4 | 10 | 31.0129 | YES | 3.69
18 | 0.5 | 67.27 | 33.635 | 23.2 | 10 | 22.5915 | YES | 3.85
19 | 0.5 | 70 | 35 | 24 | 10 | 21.426 | YES | 3.7
20 | 0.5 | 69.09 | 34.545 | 20.6 | 10 | 26.8261 | YES | 3.75
21 | 0.5 | 67.27 | 33.635 | 23.2 | 11 | 32.5908 | YES | 3.85
22 | 0.5 | 70.38 | 35.19 | 22 | 10 | 24.4572 | YES | 3.68
23 | 0.5 | 70.57 | 35.285 | 20.5 | 10 | 27.0037 | YES | 3.67
24 | 0.5 | 67.59 | 33.795 | 21.5 | 10 | 25.2786 | YES | 3.83
25 | 0.5 | 69.25 | 34.625 | 21.5 | 10 | 25.2786 | YES | 3.74
26 | 0.5 | 67.62 | 33.81 | 19.6 | 10 | 28.6552 | YES | 3.83
27 | 0.5 | 68.88 | 34.44 | 17.6 | 10 | 32.69 | YES | 3.76
28 | 0.5 | 70 | 35 | 18 | 10 | 31.8405 | YES | 3.7
29 | 0.5 | 69.62 | 34.81 | 19.1 | 10 | 29.6152 | YES | 3.72
30 | 0.5 | 70.18 | 35.09 | 16.9 | 10 | 34.2307 | YES | 3.69
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2
Note on F39: Downs Kent O: Revised version submitted to Op and DMCE. Sys did not meet required CT on 09/12/2024